{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["GC9300 Modbus-IP","GC9300 Modbus-RTU","GC9300 Modbus-ASCII"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"GC9300 Modbus-IP","index":0,"n_rows":63,"n_cols":9,"rows_kept":63,"merged":[[0,0,0,8],[2,0,2,2],[2,3,2,5],[2,6,2,8],[3,0,3,2],[3,3,3,5],[3,6,3,8],[4,0,4,2],[4,3,4,5],[4,6,4,8],[5,0,5,2],[5,3,5,5],[5,6,5,8],[7,0,7,3],[7,4,7,5]],"flags":["formulas_cached_only"]}
["GC9300 Modbus - Byteorder"]
[]
["Erstellt von: MHe"]
["Erstellt am: 01.07.2013"]
["ModbusTester: V2.5"]
["GC9300: V1.335-D-067"]
[]
["GC9300 Modbs - IP",{"$nulls":3},"ModbusTester",null,"Sollwerte","Istwerte","Ergebnis"]
["Register","Element","Datentyp","Byteorder","Datentyp","Byteorder"]
[1466,"Baujahr","int16","GC","int16","GC",2012,2012,"OK"]
[1466,"Baujahr","int16","GC","int16","ERZ",2012,2012,"OK"]
[1466,"Baujahr","int16","GC","int16","RMG-STD",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","GC",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","ERZ",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","RMG-STD",2012,2012,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","GC",809608,809608,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","ERZ",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","RMG-STD",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","GC",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","ERZ",809608,809608,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","RMG-STD",809608,809608,"OK"]
[7230,"Ho Max. Grenze","float","GC","float","GC",{"v":60000,"d":"60,000"},{"v":60000,"d":"60,000"},"OK"]
[7230,"Ho Max. Grenze","float","GC","float","ERZ","2.38e-41","2.38e-41","OK"]
[7230,"Ho Max. Grenze","float","GC","float","RMG-STD","2.38e-41","2.38e-41","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","GC","2.38e-41","2.38e-41","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","ERZ",{"v":60000,"d":"60,000"},{"v":60000,"d":"60,000"},"OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","RMG-STD",{"v":60000,"d":"60,000"},{"v":60000,"d":"60,000"},"OK"]
["-","-","int32","GC","double","GC","-","-","-"]
["-","-","int32","GC","double","ERZ","-","-","-"]
["-","-","int32","GC","double","RMG-STD","-","-","-"]
["-","-","int32","RMG-STD","double","GC","-","-","-"]
["-","-","int32","RMG-STD","double","ERZ","-","-","-"]
["-","-","int32","-","double","RMG-STD","-","-","-"]
[6520,"Messort","string","GC","ascii short","GC","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","ascii short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","GC","ascii short","RMG-STD","inBersdeimhe","inBersdeimhe","OK"]
[6520,"Messort","string","RMG-STD","ascii short","GC","inBersdeimhe","inBersdeimhe","OK"]
[6520,"Messort","string","RMG-STD","ascii short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","RMG-STD","ascii short","RMG-STD","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","unicode short","GC","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","unicode short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","GC","unicode short","RMG-STD","eBniedsrehmi","eBniedsrehmi","OK"]
[6520,"Messort","string","RMG-STD","unicode short","GC","eBniedsrehmi","eBniedsrehmi","OK"]
[6520,"Messort","string","RMG-STD","unicode short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","RMG-STD","unicode short","RMG-STD","Beindersheim","Beindersheim","OK"]
["-","-","string","GC","ascii long","GC","-","-","-"]
["-","-","string","GC","ascii long","ERZ","-","-","-"]
["-","-","string","GC","ascii long","RMG-STD","-","-","-"]
["-","-","string","RMG-STD","ascii long","GC","-","-","-"]
["-","-","string","RMG-STD","ascii long","ERZ","-","-","-"]
["-","-","string","RMG-STD","ascii long","RMG-STD","-","-","-"]
["-","-","string","GC","unicode long","GC","-","-","-"]
["-","-","string","GC","unicode long","ERZ","-","-","-"]
["-","-","string","GC","unicode long","RMG-STD","-","-","-"]
["-","-","string","RMG-STD","unicode long","GC","-","-","-"]
["-","-","string","RMG-STD","unicode long","ERZ","-","-","-"]
["-","-","string","RMG-STD","unicode long","RMG-STD","-","-","-"]
[3152,"Inbetriebnahme","time","GC","time","GC","16:00:00 13.06.2013","16:00:00 13 Jun 2013","OK"]
[3152,"Inbetriebnahme","time","GC","time","ERZ","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","GC","time","RMG-STD","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","GC","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","ERZ","16:00:00 13.06.2013","16:00:00 13 Jun 2013","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","RMG-STD","16:00:00 13.06.2013","16:00:00 13 Jun 2013","OK"]

{"sheet":"GC9300 Modbus-RTU","index":1,"n_rows":63,"n_cols":9,"rows_kept":63,"merged":[[0,0,0,8],[2,0,2,2],[2,3,2,5],[2,6,2,8],[3,0,3,2],[3,3,3,5],[3,6,3,8],[4,0,4,2],[4,3,4,5],[4,6,4,8],[5,0,5,2],[5,3,5,5],[5,6,5,8],[7,0,7,3],[7,4,7,5]],"flags":["formulas_cached_only"]}
["GC9300 Modbus - Byteorder"]
[]
["Erstellt von: MHe"]
["Erstellt am: 01.07.2013"]
["ModbusTester: V2.5"]
["GC9300: V1.335-D-067"]
[]
["GC9300 Modbs - Com5 - RTU",{"$nulls":3},"ModbusTester",null,"Sollwerte","Istwerte","Ergebnis"]
["Register","Element","Datentyp","Byteorder","Datentyp","Byteorder"]
[1466,"Baujahr","int16","GC","int16","GC",2012,2012,"OK"]
[1466,"Baujahr","int16","GC","int16","ERZ",2012,2012,"OK"]
[1466,"Baujahr","int16","GC","int16","RMG-STD",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","GC",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","ERZ",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","RMG-STD",2012,2012,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","GC",809608,809608,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","ERZ",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","RMG-STD",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","GC",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","ERZ",809608,809608,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","RMG-STD",809608,809608,"OK"]
[7230,"Ho Max. Grenze","float","GC","float","GC","60.00","60.000","OK"]
[7230,"Ho Max. Grenze","float","GC","float","ERZ","2,38e-41","2,38e-41","OK"]
[7230,"Ho Max. Grenze","float","GC","float","RMG-STD","2,38e-41","2,38e-41","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","GC","2,38e-41","2,38e-41","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","ERZ","60.00","60.000","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","RMG-STD","60.00","60.000","OK"]
["-","-","int32","GC","double","GC","-","-","-"]
["-","-","int32","GC","double","ERZ","-","-","-"]
["-","-","int32","GC","double","RMG-STD","-","-","-"]
["-","-","int32","RMG-STD","double","GC","-","-","-"]
["-","-","int32","RMG-STD","double","ERZ","-","-","-"]
["-","-","int32","RMG-STD","double","RMG-STD","-","-","-"]
[6520,"Messort","string","GC","ascii short","GC","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","ascii short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","GC","ascii short","RMG-STD","inBersdeimhe","inBersdeimhe","OK"]
[6520,"Messort","string","RMG-STD","ascii short","GC","inBersdeimhe","inBersdeimhe","OK"]
[6520,"Messort","string","RMG-STD","ascii short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","RMG-STD","ascii short","RMG-STD","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","unicode short","GC","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","unicode short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","GC","unicode short","RMG-STD","eBniedsrehmi","eBniedsrehmi","OK"]
[6520,"Messort","string","RMG-STD","unicode short","GC","eBniedsrehmi","eBniedsrehmi","OK"]
[6520,"Messort","string","RMG-STD","unicode short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","RMG-STD","unicode short","RMG-STD","Beindersheim","Beindersheim","OK"]
["-","-","string","GC","ascii long","GC","-","-","-"]
["-","-","string","GC","ascii long","ERZ","-","-","-"]
["-","-","string","GC","ascii long","RMG-STD","-","-","-"]
["-","-","string","RMG-STD","ascii long","GC","-","-","-"]
["-","-","string","RMG-STD","ascii long","ERZ","-","-","-"]
["-","-","string","RMG-STD","ascii long","RMG-STD","-","-","-"]
["-","-","string","GC","unicode long","GC","-","-","-"]
["-","-","string","GC","unicode long","ERZ","-","-","-"]
["-","-","string","GC","unicode long","RMG-STD","-","-","-"]
["-","-","string","RMG-STD","unicode long","GC","-","-","-"]
["-","-","string","RMG-STD","unicode long","ERZ","-","-","-"]
["-","-","string","RMG-STD","unicode long","RMG-STD","-","-","-"]
[3152,"Inbetriebnahme","time","GC","time","GC","16:00:00 13.06.2013","16:00:00 13.06.2013","OK"]
[3152,"Inbetriebnahme","time","GC","time","ERZ","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","GC","time","RMG-STD","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","GC","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","ERZ","16:00:00 13.06.2013","16:00:00 13.06.2013","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","RMG-STD","16:00:00 13.06.2013","16:00:00 13.06.2013","OK"]

{"sheet":"GC9300 Modbus-ASCII","index":2,"n_rows":63,"n_cols":9,"rows_kept":63,"merged":[[0,0,0,8],[2,0,2,2],[2,3,2,5],[2,6,2,8],[3,0,3,2],[3,3,3,5],[3,6,3,8],[4,0,4,2],[4,3,4,5],[4,6,4,8],[5,0,5,2],[5,3,5,5],[5,6,5,8],[7,0,7,3],[7,4,7,5]],"flags":["formulas_cached_only"]}
["GC9300 Modbus - Byteorder"]
[]
["Erstellt von: MHe"]
["Erstellt am: 02.07.2013"]
["ModbusTester: V2.5"]
["GC9300: V1.335-D-067"]
[]
["GC9300 Modbs - Com5 - RTU",{"$nulls":3},"ModbusTester",null,"Sollwerte","Istwerte","Ergebnis"]
["Register","Element","Datentyp","Byteorder","Datentyp","Byteorder"]
[1466,"Baujahr","int16","GC","int16","GC",2012,2012,"OK"]
[1466,"Baujahr","int16","GC","int16","ERZ",2012,2012,"OK"]
[1466,"Baujahr","int16","GC","int16","RMG-STD",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","GC",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","ERZ",2012,2012,"OK"]
[1466,"Baujahr","int16","RMG-STD","int16","RMG-STD",2012,2012,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","GC",809608,809608,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","ERZ",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","GC","int32","RMG-STD",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","GC",1518862348,1518862348,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","ERZ",809608,809608,"OK"]
[3040,"Messwerk Nr.","int32","RMG-STD","int32","RMG-STD",809608,809608,"OK"]
[7230,"Ho Max. Grenze","float","GC","float","GC","60.00","60.000","OK"]
[7230,"Ho Max. Grenze","float","GC","float","ERZ","2,38e-41","2,38e-41","OK"]
[7230,"Ho Max. Grenze","float","GC","float","RMG-STD","2,38e-41","2,38e-41","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","GC","2,38e-41","2,38e-41","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","ERZ","60.00","60.000","OK"]
[7230,"Ho Max. Grenze","float","RMG-STD","float","RMG-STD","60.00","60.000","OK"]
["-","-","int32","GC","double","GC","-","-","-"]
["-","-","int32","GC","double","ERZ","-","-","-"]
["-","-","int32","GC","double","RMG-STD","-","-","-"]
["-","-","int32","RMG-STD","double","GC","-","-","-"]
["-","-","int32","RMG-STD","double","ERZ","-","-","-"]
["-","-","int32","RMG-STD","double","RMG-STD","-","-","-"]
[6520,"Messort","string","GC","ascii short","GC","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","ascii short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","GC","ascii short","RMG-STD","inBersdeimhe","inBersdeimhe","OK"]
[6520,"Messort","string","RMG-STD","ascii short","GC","inBersdeimhe","inBersdeimhe","OK"]
[6520,"Messort","string","RMG-STD","ascii short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","RMG-STD","ascii short","RMG-STD","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","unicode short","GC","Beindersheim","Beindersheim","OK"]
[6520,"Messort","string","GC","unicode short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","GC","unicode short","RMG-STD","eBniedsrehmi","eBniedsrehmi","OK"]
[6520,"Messort","string","RMG-STD","unicode short","GC","eBniedsrehmi","eBniedsrehmi","OK"]
[6520,"Messort","string","RMG-STD","unicode short","ERZ","Not supported","Not supported","OK"]
[6520,"Messort","string","RMG-STD","unicode short","RMG-STD","Beindersheim","Beindersheim","OK"]
["-","-","string","GC","ascii long","GC","-","-","-"]
["-","-","string","GC","ascii long","ERZ","-","-","-"]
["-","-","string","GC","ascii long","RMG-STD","-","-","-"]
["-","-","string","RMG-STD","ascii long","GC","-","-","-"]
["-","-","string","RMG-STD","ascii long","ERZ","-","-","-"]
["-","-","string","RMG-STD","ascii long","RMG-STD","-","-","-"]
["-","-","string","GC","unicode long","GC","-","-","-"]
["-","-","string","GC","unicode long","ERZ","-","-","-"]
["-","-","string","GC","unicode long","RMG-STD","-","-","-"]
["-","-","string","RMG-STD","unicode long","GC","-","-","-"]
["-","-","string","RMG-STD","unicode long","ERZ","-","-","-"]
["-","-","string","RMG-STD","unicode long","RMG-STD","-","-","-"]
[3152,"Inbetriebnahme","time","GC","time","GC","16:00:00 13.06.2013","16:00:00 13.06.2013","OK"]
[3152,"Inbetriebnahme","time","GC","time","ERZ","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","GC","time","RMG-STD","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","GC","No valid time","No valid time","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","ERZ","16:00:00 13.06.2013","16:00:00 13.06.2013","OK"]
[3152,"Inbetriebnahme","time","RMG-STD","time","RMG-STD","16:00:00 13.06.2013","16:00:00 13.06.2013","OK"]